## Configs
| Product | Reducer | Sprinkler Type | Bracket Type | Grid Type | "D" min / max (inch) |  | "D" min / max (mm) |  | Pack and Go | Screenshot
| VS1 | VS1 | Concealed Pendent | VB2 | T Grid | 1.4 | 3 | 35.56 | 76.2 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB2-Conc-Tgrid\AQF-A-000-013_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB2-Conc-Tgrid.png
| VS1 | VS1 | Recessed Pendent | VB2 | T Grid | N/A | 2 | N/A | 50.8 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB2-Rec-Tgrid\AQF-A-000-013_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB2-Rec-Tgrid.png
| VS1 | VS1 | Concealed Pendent | VB3 | T Grid | N/A | 2.2 | N/A | 55.88 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB3-Conc-Tgrid\AQF-A-000-013_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB3-Conc-Tgrid.png
| VS1 | VS1 | Concealed Pendent | VB4 | T Grid | N/A | 2 | N/A | 50.8 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-Conc-Tgrid\AQF-A-000-013_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-Conc-Tgrid.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB4 | T Grid | 1.1 | 2.5 | 27.94 | 63.5 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-S&S-Tgrid\AQF-A-000-034_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-S&S-Tgrid.png
| VS1 | VS1 | Concealed Pendent | VB5 | Data Center Grid | 2.3 | 3.2 | 58.42 | 81.28 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Data\AQF-A-000-103_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Data.png
| VS1 | VS1 | Recessed Pendent | VB5 | Data Center Grid | 1.5 | 1.9 | 38.1 | 48.26 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Data\AQF-A-000-103_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Data.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB5 | Data Center Grid | 2.2 | 3.7 | 55.88 | 93.98 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-S&S-Data\VB5-S&S-Data-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-S&S-Data.png
Alternative (above) | VS1 | VS1 | Recessed Pendent | VB5 | Data Center Grid | 4.4 | 4.7 | 111.76 | 119.38 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Data-Above\VB5-Rec-Data-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Data-Above.png
Alternative (above) | VS1 | VS1 | Concealed Pendent | VB5 | Data Center Grid | 5.6 | 5.8 | 142.24 | 147.32 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Data-Above\VB5-Conc-Data-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Data-Above.png
Alternative (above) | VS1 | VS1 | Recessed Pendent | VB5 | Wood/Metal Joist | 4.4 | 4.7 | 111.76 | 119.38 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Joist-Above\VB5-Rec-Joist-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Joist-Above.png
| VS1 | VS1 | Recessed Pendent | VB5 | Wood/Metal Joist | N/A | 1.8 | N/A | 45.72 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Joist-Below\VB5-Rec-Joist-Below.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Joist-Below.png
Alternative (above) | VS1 | VS1 | Concealed Pendent | VB5 | Wood/Metal Joist | 5.6 | 5.8 | 142.24 | 147.32 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Joist-Above\VB5-Conc-Joist-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Joist-Above.png
| VS1 | VS1 | Concealed Pendent | VB5 | Wood/Metal Joist | N/A | 3.1 | N/A | 78.74 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Joist-Below\VB5-Conc-Joist-Below.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Joist-Below.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB5 | Wood/Metal Joist | 2.2 | 3.7 | 55.88 | 93.98 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-S&S-Joist\VB5-S&S-Joist.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-S&S-Joist.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB5 | Hat Channel | 2.1 | 3.6 | 53.34 | 91.44 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-S&S-Hat\VB5-S&S-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-S&S-Hat.png
| VS1 | VS1 | Recessed Pendent | VB5 | Hat Channel | 1.5 | 1.8 | 38.1 | 45.72 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Hat\VB5-Rec-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Hat.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB2 | T Grid | N/A | 2.2 | N/A | 55.88 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Rec-Tgrid\AQF-A-000-052_LIT-02.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Rec-Tgrid.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB2 | T Grid | N/A | 3.6 | N/A | 91.44 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Conc-Tgrid\AQF-A-000-052_LIT-02.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Conc-Tgrid.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB2 | Wood/Metal Joist | 3.6 | 4.4 | 91.44 | 111.76 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Rec-Joist\AQF-A-000-052_LIT-03.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Rec-Joist.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB2 | Wood/Metal Joist | 3.5 | 6.5 | 88.9 | 165.1 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Conc-Joist\AQF-A-000-052_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Conc-Joist.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB4 | Hat Channel | 1.3 | 2.8 | 33.02 | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Rec-Hat\AB4-Rec-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Rec-Hat.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB4 | Hat Channel | 1.3 | 4.1 | 33.02 | 104.14 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Conc-Hat\AB4-Conc-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Conc-Hat.png
| AH1/1 | 5-3/4" Straight | Recessed Pendent | AB5 | Hat Channel | 1.8 | 5 | 45.72 | 127 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Hat\AB5-Rec-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Hat.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB5 | Wood/Metal Joist | 0.8 | 5.3 | 20.32 | 134.62 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Joist\AQF-A-000-052_LIT-04.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Joist.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB5 | Wood/Metal Joist | 3.4 | 6.7 | 86.36 | 170.18 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Joist\AQF-A-000-052_LIT-05.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Joist.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB5 | Data Center Grid | N/A | 4.5 | N/A | 114.3 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Data\AB5-Rec-Data.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Data.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB5 | Data Center Grid | 3.2 | 7.5 | 81.28 | 190.5 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Data\AQF-A-000-052_LIT-07.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Data.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB7 | T Grid | N/A | 2.8 | N/A | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Rec-Tgrid\AB7-Rec-Tgrid-Final.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Rec-Tgrid.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB7 | T Grid | N/A | 4 | N/A | 101.6 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Conc-Tgrid\AB7-Conc_Tgrid.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Conc-Tgrid.png
| AH1/2 | Low profile Long Elbow | Recessed Pendent | AB11 | T Grid | N/A | 2.6 | N/A | 66.04 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB11-Rec-Tgrid\AB11-Rec-Tgrid.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB11-Rec-Tgrid-Low-Long.png
| AH1/2 | Low profile Short Elbow | Concealed Pendent | AB11 | T Grid | 1 | 2.3 | 25.4 | 58.42 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB11-Conc-Tgrid\AB11-Conc-Tgrid.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB11-Conc-Tgrid.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB2 | T Grid | 1.4 | 2.3 | 35.56 | 58.42 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Rec-Tgrid-Stand-Long\AB2-Rec-Tgrid-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Rec-Tgrid-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB2 | T Grid | 1.4 | 1.9 | 35.56 | 48.26 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Conc-Tgrid-Stand-Short\Ab2-Conc-Tgrid-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Conc-Tgrid-Stand-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB4 | Hat Channel | 1.3 | 2.7 | 33.02 | 68.58 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Rec-Hat-Stand-Long\AB4-Rec-Hat-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Rec-Hat-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB4 | Hat Channel | 1.3 | 2.3 | 33.02 | 58.42 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Conc-Hat-Stand-Short\AB4-Conc-Hat-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Conc-Hat-Stand-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB5 | Hat Channel | 1.8 | 5 | 45.72 | 127 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Hat-Stand-Long\AB5-Rec-Hat-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Hat-Stand-Long.png
| AH1/2 | Low profile Long Elbow | Recessed Pendent | AB5 | Data Center Grid | N/A | 3.8 | N/A | 96.52 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Data-Low Profile-Long\AB5-Rec-Data-Low-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Data-Low-Long.png
| AH1/2 | Low profile Short Elbow | Concealed Pendent | AB5 | Data Center Grid | 2.1 | 3.5 | 53.34 | 88.9 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Data-Low-Short\AB5-Conc-Low-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Data-Low-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB5 | Data Center Grid | 2.1 | 5.1 | 53.34 | 129.54 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Data-Stand-Long\AB5-Rec-Data-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Data-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB5 | Data Center Grid | 3.2 | 5.3 | 81.28 | 134.62 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Data-Stand-Short\AB5-Conc-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Data-Stand-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB7 | T Grid | 1.5 | 2.8 | 38.1 | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Rec-Tgrid-Stand-Long\AB7-Rec-Tgrid-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Rec-Tgrid-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB7 | T Grid | 1.5 | 2.5 | 38.1 | 63.5 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Conc-Tgrid-Stand-Short\AB7-Conc-Tgrid-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Conc-Tgrid-Stand-Short.png
| AQD-M | AQD-M | Pendent | AQD Round 8-12" | Round Metal Duct | 8 | 12 | 203.2 | 304.8 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AQD Round Duct\AQD Round Duct.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AQD Round Duct.png
| AQD-M | AQD-M | Pendent | AQD Round 13-16" | Round Metal Duct | 13 | 16 | 330.2 | 406.4 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AQD Round Duct\AQD Round Duct.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AQD Round Duct.png
| AQD-M | AQD-M | Pendent | AQD Round 17-22" | Round Metal Duct | 17 | 22 | 431.8 | 558.8 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AQD Round Duct\AQD Round Duct.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AQD Round Duct.png
| AQD-M | AQD-M | Pendent | AQD Flat | Square Metal Duct | N/A | N/A | N/A | N/A | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AQD Square Duct\AQD Square Duct.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AQD Square Duct.png
| GH1-C2C | 12" N/148 | Pendent | AB6-W | Insulated Metal Panel | 2 | 7 | 50 | 177.8 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\GH1-Panel\GH1-Panel.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\GH1-Panel.png

## Cleanroom Configs
GRID MFG | GRID MODEL | GRID HEIGHT | Pack & Go | Screenshot 1 | Screenshot 2 | Screenshot 3 | Screenshot 4 | Screenshot 1 | Screenshot 3
Exyte | 55/70TE | 2.76" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Exyte 55 70 TE\AQC UNIV-Exyte 5570 TE.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 5570 TE-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 5570 TE-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 5570 TE-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 5570 TE-4.png | #VALUE! | #VALUE!
| 55/100TE | 3.94" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Exyte 55 100 TE\AQC UNIV-Exyte 55 100 TE.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 100 TE-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 100 TE-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 100 TE-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 100 TE-4.png
| 55/130TE | 5.12" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Exyte 55 130 TE\AQC UNIV-Exyte 55 130 TE.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 130 TE-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 130 TE-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 130 TE-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 130 TE-4.png
| 55/240TE | 9.45" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Exyte 55 240 TE\AQC UNIV-Exyte 55 240 TE.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 240 TE-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 240 TE-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 240 TE-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Exyte 55 240 TE-4.png
| Red Pedestal | 3.0"
Gordon | DS-20 | 1.375" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Gordon DS20\AQC UNIV-Gordon DS20.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon DS20-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon DS20-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon DS20-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon DS20-4.png
| WG-38 | 3.0" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Gordon WG38\AQC UNIV-Gordon WG38.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WG38-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WG38-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WG38-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WG38-4.png
| WG-XTR | 3.19" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Gordon WGXTR\AQC UNIV-Gordon WGXTR.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WGXTR-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WGXTR-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WGXTR-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Gordon WGXTR-4.png
Nortek | CleanPak | 3.625"
| FlexTrak | 5.0" | [5 empty] | Screenshot 2
AJ MFG | Micro-T | 1.5" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\AJ Micro T\AQC UNIV-AJ Micro T.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro T-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro T-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro T-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro T-4.png | #VALUE!
| Micro-TW | 3.0" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\AJ Micro TW\AQC UNIV-AJ MicroTW.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro TW-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro TW-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro TW-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-AJ Micro TW-4.png
BASX | CL0018 | 5.5" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\BASX CL0018\AQC UNIV-BASX CL0018.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-BASX CL0018-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-BASX CL0018-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-BASX CL0018-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-BASX CL0018-4.png
Pophen | CK 2000-H55 | 55mm | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Pophen CK2000 H55\AQC UNIV-Pophen CK2000 H55.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H55-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H55-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H55-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H55-4.png
| CK 2000-H70 | 70mm | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Pophen CK2000 H70\AQC UNIV-Pophen CK2000 H70.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H70-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H70-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H70-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H70-4.png
| CK 2000-H100 | 100mm | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Pohen CK2000 H100\AQC UNIV-Pophen CK2000 H100.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H100-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H100-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H100-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H100-4.png |  | Screenshot 4
| CK 2000-H130 | 130mm | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Pophen CK2000 H130\AQC UNIV-Pophen CK2000 H130.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H130-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H130-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H130-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Pophen CK2000 H130-4.png |  | #VALUE!
Daldrop/SBB/Gorilla Grid | 2025 | 2.5" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Daldrop 2025\AQC UNIV-Daldrop 2025.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2025-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2025-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2025-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2025-4.png
| 2035 | 3.5" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Daldrop 2035\AQC UNIV-Daldrop 2035.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2035-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2035-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2035-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2035-4.png
| 2045 | 4.5" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Daldrop 2045\AQC UNIV-Daldrop 2045.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2045-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2045-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2045-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2045-4.png
| 2055 | 5.5" | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Pack and Go\Daldrop 2055\AQC UNIV-Daldrop 2055.SLDASM | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2055-1.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2055-2.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2055-3.png | \\en-svr-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Cleanroom\Screenshots\AQC UNIV-Daldrop 2055-4.png
| PH120 | 4.72"
CLIN | HD55 | 2.76"
| HD65 | 3.21"
UG Ceilings | UG-2
UG-1
| UG-Lite | 4" w/ port bracket
Long Sight and Sunway | Long Sight | 68mm
| Sunway | 68mm

## Wish List
Wish List
| Product | Reducer | Sprinkler Type | Bracket Type | Grid Type | "D" min / max (inch) |  | "D" min / max (mm) |  | Assem P&G | SS P&G
| AH1/AH2 | Standard Long Elbow | Concealed | AB2 | T Grid
| AH1/AH2 | Standard Long Elbow | Concealed | AB4 | Hat Channel
| AH1/AH2 | Standard Long Elbow | Concealed | AB5 | Data Center Grid
| AH1/AH2 | Standard Long Elbow | Concealed | AB7 | T Grid
Metlworks Ceiling | VS1 | VS1 | Concealed Pendent | VB4 | T Grid | 5.7 | 5.9 | 144.78 | 149.86 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-Conc-Tgrid-MetalWorks\VB4-Conc-Tgrid-MetalWorks.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-Conc-Tgrid-MetalWorks.png
Metlworks Ceiling | VS1 | VS1 | Recessed Pendent | VB4 | T Grid | 4.4 | 4.6 | 111.76 | 116.84 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-Rec-Tgrid-MetalWorks\VB4-Rec-Tgrid-MetalWorks.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-Rec-Tgrid-MetalWorks.png

## Notes
Add note on recessed pendents: "Values provided are for 3/4" adjustment escutcheon"
Add note to all AH1/AH2 recessed pendents: "Values provided are for V2708 sprinkler, values may be different for other sprinklers"
Add note to all AH1/AH2 concealed pendents: "Values provided are for V3802 sprinkler, values may be different for other sprinklers"

## Beta feedback
Bicket
Add full line of reducers (9" and 13" straight) - Bicket
I think AB6 and AB6W would definitely be a benefit.
On wood and metal “grid type” is there any way to use different elevations? (ie. 2x6 or 2x8 wood studs & 1-5/8” C-Channel)
I’ve been running into this a lot in lately in multi-family
More measures or dimensions would be extremely helpful (ie. dimensions of the specific head or how much the set-screw sits down below the gate etc.)
Any plans for the AQC-U or Duct Assemblies would be awesome
Maybe a less generic “data center grid” description and go with the actual manufacturer/ model (with dimensions and required screw/ anchoring method)
A thought about this as well… 24” vs 48” options as we are really running into some weird DC applications
For example 6’x8’ Pics Pollargy “squares” with standard 2’x4’ T-Bar in-fill grid
In this unique situation it would be awesome to mock up a 4’ bar stock with an AB2 end bracket on one side and an AB5 end bracket on the other
it would be super helpful if we could list ceiling mfg with appropriate model name/bracket fit up. Is that doable? (Waddell)
we would need to have authorization and access to CAD models for all of the different grid makes/models if we are going to use their products in our tool and I know we ran into roadblocks with that already so this was path to get something implemented
Adding "C" clearance height above grid to top of hose/elbow (Kvistad)