## Configs
| Product | Reducer | Sprinkler Type | Bracket Type | Grid Type | "D" min / max (inch) |  | "D" min / max (mm) |  | Pack and Go | Screenshot
| VS1 | VS1 | Concealed Pendent | VB2 | T Grid | 1.4 | 3 | 35.56 | 76.2 | "\\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB2-Conc-Tgrid\AQF-A-000-013_LIT-01.SLDASM" | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB2-Conc-Tgrid.png
| VS1 | VS1 | Recessed Pendent | VB2 | T Grid | N/A | 2 | N/A | 50.8 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB2-Rec-Tgrid\AQF-A-000-013_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB2-Rec-Tgrid.png
| VS1 | VS1 | Concealed Pendent | VB3 | T Grid | N/A | 2.2 | N/A | 55.88 | "\\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB3-Conc-Tgrid\AQF-A-000-013_LIT-01.SLDASM" | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB3-Conc-Tgrid.png
| VS1 | VS1 | Concealed Pendent | VB4 | T Grid | N/A | 2 | N/A | 50.8 | "\\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-Conc-Tgrid\AQF-A-000-013_LIT-01.SLDASM" | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-Conc-Tgrid.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB4 | T Grid | 1.1 | 2.5 | 27.94 | 63.5 | "\\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-S&S-Tgrid\AQF-A-000-034_LIT-01.SLDASM" | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-S&S-Tgrid.png
| VS1 | VS1 | Concealed Pendent | VB5 | Data Center Grid | 2.3 | 3.2 | 58.42 | 81.28 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Data\AQF-A-000-103_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Data.png
| VS1 | VS1 | Recessed Pendent | VB5 | Data Center Grid | 1.5 | 1.9 | 38.1 | 48.26 | "\\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Data\AQF-A-000-103_LIT-01.SLDASM" | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Data.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB5 | Data Center Grid | 2.2 | 3.7 | 55.88 | 93.98 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-S&S-Data\VB5-S&S-Data-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-S&S-Data.png
Alternative (above) | VS1 | VS1 | Recessed Pendent | VB5 | Data Center Grid | 4.4 | 4.7 | 111.76 | 119.38 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Data-Above\VB5-Rec-Data-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Data-Above.png
Alternative (above) | VS1 | VS1 | Concealed Pendent | VB5 | Data Center Grid | 5.6 | 5.8 | 142.24 | 147.32 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Data-Above\VB5-Conc-Data-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Data-Above.png
Alternative (above) | VS1 | VS1 | Recessed Pendent | VB5 | Wood/Metal Joist | 4.4 | 4.7 | 111.76 | 119.38 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Joist-Above\VB5-Rec-Joist-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Joist-Above.png
| VS1 | VS1 | Recessed Pendent | VB5 | Wood/Metal Joist | N/A | 1.8 | N/A | 45.72 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Joist-Below\VB5-Rec-Joist-Below.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Joist-Below.png
Alternative (above) | VS1 | VS1 | Concealed Pendent | VB5 | Wood/Metal Joist | 5.6 | 5.8 | 142.24 | 147.32 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Joist-Above\VB5-Conc-Joist-Above.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Joist-Above.png
| VS1 | VS1 | Concealed Pendent | VB5 | Wood/Metal Joist | N/A | 3.1 | N/A | 78.74 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Conc-Joist-Below\VB5-Conc-Joist-Below.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Conc-Joist-Below.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB5 | Wood/Metal Joist | 2.2 | 3.7 | 55.88 | 93.98 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-S&S-Joist\VB5-S&S-Joist.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-S&S-Joist.png
| VS1 | VS1 | Sleeve & Skirt Pendent | VB5 | Hat Channel | 2.1 | 3.6 | 53.34 | 91.44 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-S&S-Hat\VB5-S&S-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-S&S-Hat.png
| VS1 | VS1 | Recessed Pendent | VB5 | Hat Channel | 1.5 | 1.8 | 38.1 | 45.72 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB5-Rec-Hat\VB5-Rec-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB5-Rec-Hat.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB2 | T Grid | N/A | 2.8 | N/A | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Rec-Tgrid\AQF-A-000-052_LIT-02.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Rec-Tgrid.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB2 | T Grid | N/A | 3.6 | N/A | 91.44 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Conc-Tgrid\AQF-A-000-052_LIT-02.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Conc-Tgrid.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB2 | Wood/Metal Joist | 3.6 | 4.4 | 91.44 | 111.76 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Rec-Joist\AQF-A-000-052_LIT-03.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Rec-Joist.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB2 | Wood/Metal Joist | 3.5 | 6.5 | 88.9 | 165.1 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Conc-Joist\AQF-A-000-052_LIT-01.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Conc-Joist.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB4 | Hat Channel | 1.3 | 2.8 | 33.02 | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Rec-Hat\AB4-Rec-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Rec-Hat.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB4 | Hat Channel | 1.3 | 4.1 | 33.02 | 104.14 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Conc-Hat\AB4-Conc-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Conc-Hat.png
| AH1/1 | 5-3/4" Straight | Recessed Pendent | AB5 | Hat Channel | 1.8 | 5 | 45.72 | 127 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Hat\AB5-Rec-Hat.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Hat.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB5 | Wood/Metal Joist | 0.8 | 5.3 | 20.32 | 134.62 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Joist\AQF-A-000-052_LIT-04.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Joist.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB5 | Wood/Metal Joist | 3.4 | 6.7 | 86.36 | 170.18 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Joist\AQF-A-000-052_LIT-05.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Joist.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB5 | Data Center Grid | N/A | 4.5 | N/A | 114.3 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Data\AB5-Rec-Data.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Data.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB5 | Data Center Grid | 3.2 | 7.5 | 81.28 | 190.5 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Data\AQF-A-000-052_LIT-07.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Data.png
| AH1/2 | 5-3/4" Straight | Recessed Pendent | AB7 | T Grid | N/A | 2.8 | N/A | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Rec-Tgrid\AB7-Rec-Tgrid-Final.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Rec-Tgrid.png
| AH1/2 | 5-3/4" Straight | Concealed Pendent | AB7 | T Grid | N/A | 4 | N/A | 101.6 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Conc-Tgrid\AB7-Conc_Tgrid.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Conc-Tgrid.png
| AH1/2 | Low profile Long Elbow | Recessed Pendent | AB11 | T Grid | N/A | 2.7 | N/A | 68.58 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB11-Rec-Tgrid\AB11-Rec-Tgrid.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB11-Rec-Tgrid-Low-Long.png
| AH1/2 | Low profile Short Elbow | Concealed Pendent | AB11 | T Grid | 1 | 2.3 | 25.4 | 58.42 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB11-Conc-Tgrid\AB11-Conc-Tgrid.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB11-Conc-Tgrid.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB2 | T Grid | 1.4 | 2.3 | 35.56 | 58.42 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Rec-Tgrid-Stand-Long\AB2-Rec-Tgrid-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Rec-Tgrid-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB2 | T Grid | 1.4 | 1.9 | 35.56 | 48.26 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB2-Conc-Tgrid-Stand-Short\Ab2-Conc-Tgrid-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB2-Conc-Tgrid-Stand-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB4 | Hat Channel | 1.3 | 2.7 | 33.02 | 68.58 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Rec-Hat-Stand-Long\AB4-Rec-Hat-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Rec-Hat-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB4 | Hat Channel | 1.3 | 2.3 | 33.02 | 58.42 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB4-Conc-Hat-Stand-Short\AB4-Conc-Hat-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB4-Conc-Hat-Stand-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB5 | Hat Channel | 1.8 | 5 | 45.72 | 127 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Hat-Stand-Long\AB5-Rec-Hat-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Hat-Stand-Long.png
| AH1/2 | Low profile Long Elbow | Recessed Pendent | AB5 | Data Center Grid | N/A | 3.8 | N/A | 96.52 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Data-Low Profile-Long\AB5-Rec-Data-Low-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Data-Low-Long.png
| AH1/2 | Low profile Short Elbow | Concealed Pendent | AB5 | Data Center Grid | 2.1 | 3.5 | 53.34 | 88.9 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Data-Low-Short\AB5-Conc-Low-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Data-Low-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB5 | Data Center Grid | 2.1 | 5.1 | 53.34 | 129.54 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Rec-Data-Stand-Long\AB5-Rec-Data-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Rec-Data-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB5 | Data Center Grid | 3.2 | 5.3 | 81.28 | 134.62 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB5-Conc-Data-Stand-Short\AB5-Conc-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB5-Conc-Data-Stand-Short.png
| AH1/2 | Standard Long Elbow | Recessed Pendent | AB7 | T Grid | N/A | 2.8 | N/A | 71.12 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Rec-Tgrid-Stand-Long\AB7-Rec-Tgrid-Stand-Long.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Rec-Tgrid-Stand-Long.png
| AH1/2 | Standard Short Elbow | Concealed Pendent | AB7 | T Grid | 1.5 | 2.5 | 38.1 | 63.5 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\AB7-Conc-Tgrid-Stand-Short\AB7-Conc-Tgrid-Stand-Short.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\AB7-Conc-Tgrid-Stand-Short.png

## Wish List
Wish List
| Product | Reducer | Sprinkler Type | Bracket Type | Grid Type |  |  |  |  | Assem P&G | SS P&G
| AH1/AH2 | Standard Long Elbow | Concealed | AB2 | T Grid
| AH1/AH2 | Standard Long Elbow | Concealed | AB4 | Hat Channel
| AH1/AH2 | Standard Long Elbow | Concealed | AB5 | Data Center Grid
| AH1/AH2 | Standard Long Elbow | Concealed | AB7 | T Grid
Metlworks Ceiling | VS1 | VS1 | Concealed Pendent | VB4 | T Grid | 5.7 | 5.9 | 144.78 | 149.86 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-Conc-Tgrid-MetalWorks\VB4-Conc-Tgrid-MetalWorks.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-Conc-Tgrid-MetalWorks.png
Metlworks Ceiling | VS1 | VS1 | Recessed Pendent | VB4 | T Grid | 4.4 | 4.6 | 111.76 | 116.84 | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Pack and Go Model Files\VB4-Rec-Tgrid-MetalWorks\VB4-Rec-Tgrid-MetalWorks.SLDASM | \\EN-SVR-4\CorpEng\Fire Safety\Sustaining Projects\VicFlex Bracket Calculator\Screenshots\VB4-Rec-Tgrid-MetalWorks.png

## Notes
Ability to filter by product, reducer, sprinkler, bracket, grid
Ability to filter by measurement (top of grid to ceiling face)
Change "VB6" to "VB5"
Add metric units
Add note on recessed pendents: "Values provided are for 3/4" adjustment escutcheon"
Add note to all AH1/AH2 recessed pendents: "Values provided are for V2708 sprinkler, values may be different for other sprinklers"
Add note to all AH1/AH2 concealed pendents: "Values provided are for V3802 sprinkler, values may be different for other sprinklers"
Add note to all: "The "D" dimension is defined as the distance from top of ceiling to finished ceiling panel face"